SOLAR EPC COST ESTIMATION

# Gennex Technologies
1MW, 5MW and 10MW Solar Stations

Methodology, calculations, assumptions and indicative turnkey pricing

Prepared as an independent preliminary budget model

Date: 16 July 2026

IMPORTANT This document is not a Gennex quotation. It reconstructs a likely EPC price using publicly visible Gennex product prices, disclosed project capabilities and engineering allowances for components whose utility-scale prices are not published.

Prepared for preliminary planning and vendor negotiation

# Executive Summary

Objective. To explain how the indicative prices for complete 1MW, 5MW and 10MW solar stations were generated, including equipment quantities, cost allowances, economies of scale, battery additions and exclusions.

| Capacity | Estimated turnkey range | Planning figure | Basis |
| --- | --- | --- | --- |
| 1MWp | ₦0.90bn–₦1.50bn | ₦1.30bn | Bottom-up equipment and EPC allowances |
| 5MWp | ₦4.20bn–₦6.80bn | ₦5.50bn | 1MW range scaled with 7%–10% discount |
| 10MWp | ₦7.70bn–₦12.30bn | ₦10.20bn | 1MW range scaled with 14%–18% discount |

Interpretation: The ranges are intended for budgeting. A final price requires a site survey, load profile, geotechnical information, grid interconnection design, exact battery duration and a formal bill of quantities from Gennex.

## How the estimate was built

| 1 | Verify Gennex scope: Confirm that the company sells, distributes, designs, installs and maintains solar systems. |
| --- | --- |

| 2 | Anchor equipment prices: Use visible prices for a 725W Jinko module, a 12kW Gennex inverter and a 16kWh lithium battery. |
| --- | --- |

| 3 | Calculate equipment quantities: Divide the required plant capacity by the capacity of each module or device and round up to whole units. |
| --- | --- |

| 4 | Add balance-of-plant costs: Estimate mounting, cabling, protection, transformer, civil works, engineering, logistics and contractor margin. |
| --- | --- |

| 5 | Apply scale discounts: Reduce cost per MW for 5MW and 10MW because procurement, engineering and mobilisation are shared across more capacity. |
| --- | --- |

| 6 | Add storage separately: Price batteries in MWh because a solar plant’s MW rating does not specify how many hours it can supply power after sunset. |
| --- | --- |

# 1. Source Evidence Used

Company capability. Gennex describes itself as a Nigerian solar company specialising in the sales, distribution and installation of solar products, with design, execution, installation and maintenance capabilities. This supports treating the estimate as a potential turnkey EPC scope rather than equipment supply only. [1]

Commercial project evidence. Gennex’s project pages identify a 100kW Petrocam installation at Mowe and several other Petrocam sites. This demonstrates commercial execution experience, although the website does not publish a completed single-site 1MW quotation. [2][3]

Visible retail anchors. The public web pages used for the model showed a 725W Jinko bifacial module at ₦187,000, a Gennex Plus 12kW inverter at ₦1,457,000 and a 16kWh lithium battery at ₦2,660,000. These are retail reference points, not confirmed utility-scale bulk quotations. [4][5][6]

| Evidence item | Public reference | How it was used | Limitation |
| --- | --- | --- | --- |
| Gennex service scope | Sales, distribution, design, installation and maintenance | Defines likely turnkey project scope | Exact EPC inclusions must be confirmed |
| 725W Jinko module | ₦187,000 each | Calculates panel quantity and retail module cost | Bulk order may receive a discount |
| 12kW inverter | ₦1,457,000 each | Provides a modular inverter cost benchmark | A 1MW plant should normally use utility-scale string/central inverters |
| 16kWh lithium battery | ₦2,660,000 each | Builds module-only storage cost per MWh | Utility BESS also needs PCS, BMS, HVAC and fire protection |
| Petrocam projects | 100kW and multi-site projects | Supports commercial installation capability | Not evidence of a published 1MW price |

# 2. Key Technical Assumptions

• Capacity basis: The main estimates are for MWp of installed DC solar-module capacity. A requirement stated as MWAC may require additional panels.

• Installation type: Ground-mounted commercial/utility system on a reasonably accessible site.

• Battery: Excluded from the base solar price and added separately in MWh.

• Grid works: Normal transformer and switchgear allowance is included; major transmission lines or a large new substation are excluded.

• Taxes and financing: VAT, financing interest, land purchase and extraordinary statutory costs are excluded unless stated otherwise.

• Price status: Gennex online prices and market conditions can change; the estimate is dated 16 July 2026.

# 3. Detailed 1MW Calculation

## 3.1 Solar-module quantity and cost

Formula: Required number of panels = Required DC capacity (W) ÷ Panel rating (W), rounded up to the next whole panel.

| 1MW panel quantity | 1,000,000W ÷ 725W = 1,379.31 panels Round up to 1,380 panels, giving 1,000,500W or 1.0005MWp. |
| --- | --- |

Retail module cost: 1,380 × ₦187,000 = ₦258.06 million

Bulk-price allowance: Because Gennex advertises wholesale supply, a 10% bulk discount was used only for the low-cost scenario: ₦258.06m × 90% = approximately ₦232.25m. The module allowance was therefore rounded to ₦232m–₦258m.

## 3.2 Inverter benchmark

Retail modular check: 1,000kW ÷ 12kW = 83.33 units, rounded to 84 units. This gives approximately 1,008kW of nominal inverter capacity.

84 × ₦1,457,000 = ₦122.39 million.

Why the inverter range is wider than ₦122.39m: The 12kW products provide a price anchor, but a professional 1MW plant would usually use larger three-phase string or central inverters, specialised protection, communications and possibly hybrid functionality. The estimate therefore uses ₦120m–₦250m.

## 3.3 Balance-of-plant and EPC allowances

The online store does not publish a utility-scale bill of quantities. The remaining categories were estimated as engineering allowances based on the physical scope required to turn panels and inverters into an operational plant. These allowances are intentionally broad because site and interconnection conditions are unknown.

| Cost category | Low estimate | High estimate | Calculation basis |
| --- | --- | --- | --- |
| Solar modules | ₦232m | ₦258m | 725W panel retail price with 0%–10% bulk discount |
| Inverter system | ₦120m | ₦250m | 12kW retail benchmark plus utility-scale design uncertainty |
| Mounting and foundations | ₦90m | ₦150m | Steel/aluminium structures, piles or concrete, installation |
| DC/AC cables and protection | ₦75m | ₦140m | Cables, combiner boxes, breakers, SPD, earthing |
| Transformer, switchgear and metering | ₦80m | ₦160m | Voltage transformation, distribution and protection |
| Site works and security | ₦60m | ₦120m | Clearing, roads, drainage, fencing and basic security |
| Engineering, installation and commissioning | ₦70m | ₦140m | Design, labour, testing, documentation and handover |
| Logistics and mobilisation | ₦25m | ₦60m | Transport, handling, mobilisation and insurance allowance |
| Overhead, profit and contingency | ₦90m | ₦180m | Contractor margin and unknown project risks |
| DETAILED TOTAL | ₦842m | ₦1.458bn | Sum of all categories |
| ROUNDED BUDGET RANGE | ₦900m | ₦1.500bn | Rounded upward for preliminary budget protection |

Result: The detailed calculation produced ₦842m–₦1.458bn. This was rounded to ₦900m–₦1.50bn because early-stage estimates should not imply false precision and should retain protection against site-specific cost increases.

# 4. Scaling the Estimate to 5MW and 10MW

Why the 1MW price was not simply multiplied. Larger projects normally reduce cost per MW through bulk equipment purchasing and the sharing of design, mobilisation, project management, monitoring, site facilities and commissioning costs. The model therefore applies modest scale discounts rather than assuming a perfectly linear relationship. IRENA’s cost reporting also identifies scale and procurement as important drivers of utility-scale renewable project costs. [7]

## 4.1 Panel quantities at each capacity

| Plant size | Formula | Panels | Actual DC capacity | Retail panel value |
| --- | --- | --- | --- | --- |
| 1MW | 1,000,000 ÷ 725 | 1,380 | 1.0005MWp | ₦258.06m |
| 5MW | 5,000,000 ÷ 725 | 6,897 | 5.000325MWp | ₦1.289739bn |
| 10MW | 10,000,000 ÷ 725 | 13,794 | 10.00065MWp | ₦2.579478bn |

## 4.2 Economy-of-scale formulas

General formula: Scaled project cost = 1MW budget × Project capacity × (1 − Scale discount).

| Scenario | Base calculation | Discount applied | Calculated result | Rounded range |
| --- | --- | --- | --- | --- |
| 5MW low | ₦0.90bn × 5 × 93% | 7% | ₦4.185bn | ₦4.20bn |
| 5MW high | ₦1.50bn × 5 × 90% | 10% | ₦6.750bn | ₦6.80bn |
| 10MW low | ₦0.90bn × 10 × 86% | 14% | ₦7.740bn | ₦7.70bn |
| 10MW high | ₦1.50bn × 10 × 82% | 18% | ₦12.300bn | ₦12.30bn |

Discount selection. A larger discount was applied to the high-cost end because that end contains more overhead, contingency and project-risk allowances that are unlikely to rise at the same rate as capacity. The discounts are modelling assumptions, not discounts quoted by Gennex.

## 4.3 Recommended planning figures

| Capacity | Range midpoint | Selected planning figure | Reason for selection |
| --- | --- | --- | --- |
| 1MW | ₦1.20bn | ₦1.30bn | Slightly above midpoint to protect against site and interconnection uncertainty |
| 5MW | ₦5.50bn | ₦5.50bn | Midpoint provides balanced preliminary budget |
| 10MW | ₦10.00bn | ₦10.20bn | Modest protection above midpoint for utility interconnection complexity |

# 5. Battery Storage Calculation

Storage is priced separately because MW and MWh measure different things. MW is the maximum rate of power delivery; MWh is the amount of energy stored. For example, a 5MW/10MWh battery can theoretically supply 5MW for approximately two hours before allowing for reserve limits and system losses.

## 5.1 Retail battery-module benchmark

Published reference: 16kWh lithium battery at ₦2.66m.

Module-only cost per kWh = ₦2,660,000 ÷ 16kWh = ₦166,250/kWh.

| Storage | Units required | Module cost | Integrated BESS allowance | What the extra allowance covers |
| --- | --- | --- | --- | --- |
| 1MWh | 63 × 16kWh | ₦167.58m | ₦210m–₦260m | PCS, racks, BMS, EMS, HVAC, fire protection, cabling and commissioning |
| 5MWh | 313 units approx. | ₦832.58m | ₦1.05bn–₦1.30bn | Scaled integrated system allowance |
| 10MWh | 625 units | ₦1.6625bn | ₦2.10bn–₦2.60bn | Scaled integrated system allowance |
| 20MWh | 1,250 units | ₦3.325bn | ₦4.20bn–₦5.20bn | Scaled integrated system allowance |
| 40MWh | 2,500 units | ₦6.650bn | ₦8.40bn–₦10.40bn | Scaled integrated system allowance |

## 5.2 Solar-plus-storage totals

| Solar plant | Storage duration example | Calculation | Estimated project range |
| --- | --- | --- | --- |
| 5MW | No storage | ₦4.20bn–₦6.80bn | ₦4.20bn–₦6.80bn |
| 5MW + 5MWh | Approx. 1 hour | Solar + ₦1.05bn–₦1.30bn | ₦5.25bn–₦8.10bn |
| 5MW + 10MWh | Approx. 2 hours | Solar + ₦2.10bn–₦2.60bn | ₦6.30bn–₦9.40bn |
| 5MW + 20MWh | Approx. 4 hours | Solar + ₦4.20bn–₦5.20bn | ₦8.40bn–₦12.00bn |
| 10MW | No storage | ₦7.70bn–₦12.30bn | ₦7.70bn–₦12.30bn |
| 10MW + 10MWh | Approx. 1 hour | Solar + ₦2.10bn–₦2.60bn | ₦9.80bn–₦14.90bn |
| 10MW + 20MWh | Approx. 2 hours | Solar + ₦4.20bn–₦5.20bn | ₦11.90bn–₦17.50bn |
| 10MW + 40MWh | Approx. 4 hours | Solar + ₦8.40bn–₦10.40bn | ₦16.10bn–₦22.70bn |

# 6. Factors That Can Change the Estimate

## 6.1 MWp versus MWAC

The estimates above assume MWp of panel capacity. When the required capacity is stated as MWAC, the designer may install more DC panel capacity than inverter capacity. A DC:AC ratio of 1.3 means 30% more module nameplate capacity than inverter capacity. [8]

| Required output | Assumed DC:AC ratio | Possible panel capacity | Effect on budget |
| --- | --- | --- | --- |
| 1MWAC | 1.30 | 1.30MWp | More modules, mounting, cables and possibly land |
| 5MWAC | 1.30 | 6.50MWp | Could raise total project price by roughly 20%–30%, depending on design |
| 10MWAC | 1.30 | 13.00MWp | Could raise total project price by roughly 20%–30%, depending on design |

## 6.2 Main cost sensitivities

• Site condition: Rocky ground, flooding, weak soil or difficult access can increase civil and foundation costs.

• Grid connection: A long interconnection line, high-voltage bay or major substation can add hundreds of millions or more.

• Imported equipment and currency: Panels, inverters and batteries are exposed to exchange-rate, freight and customs changes.

• System architecture: Off-grid and hybrid plants need more control, storage, redundancy and protection than simple grid-tied systems.

• Warranty and performance guarantees: Longer warranty, availability guarantees, bonds and liquidated damages can increase contractor pricing.

• Location and security: Remote sites may require greater transport, accommodation, fencing, CCTV and security expenditure.

## 6.3 Likely exclusions

| • Land purchase or long-term lease | • VAT and financing interest |
| --- | --- |
| • Environmental and grid-impact studies | • Major transmission line or distribution-network extension |
| • Large new high-voltage substation | • Community compensation and right-of-way payments |
| • Operations and maintenance after the included warranty period | • Extraordinary security or remote-site accommodation |

# 7. Information Required for a Formal Gennex Quotation

To replace the estimate with a reliable contract price, the request for quotation should require the following:

| 1 | State whether capacity means MWp DC or MWAC export capacity. |
| --- | --- |

| 2 | Provide the exact site location, coordinates, land area and ownership status. |
| --- | --- |

| 3 | Provide at least 12 months of electricity consumption and maximum-demand data. |
| --- | --- |

| 4 | State whether the plant will be on-grid, off-grid or hybrid with generators. |
| --- | --- |

| 5 | Specify required battery power in MW and usable energy in MWh. |
| --- | --- |

| 6 | Request an itemised bill of quantities with brand, model, rating and quantity. |
| --- | --- |

| 7 | Request expected annual energy yield, performance ratio and degradation assumptions. |
| --- | --- |

| 8 | Request transformer, switchgear, cable and protection specifications. |
| --- | --- |

| 9 | Request civil scope, drainage, fencing, roads, security and site-preparation details. |
| --- | --- |

| 10 | Request warranties for modules, inverters, batteries and installation workmanship. |
| --- | --- |

| 11 | Request project programme, payment milestones and quotation-validity period. |
| --- | --- |

| 12 | Request a clear schedule of inclusions, exclusions, taxes and owner-supplied items. |
| --- | --- |

# 8. Final Budget Recommendation

| Project | Working budget | Suggested approval ceiling before site survey |
| --- | --- | --- |
| 1MWp | ₦1.30bn | Approximately ₦1.50bn, excluding major grid extension and battery |
| 5MWp | ₦5.50bn | Approximately ₦7.00bn, excluding major grid extension and battery |
| 10MWp | ₦10.20bn | Approximately ₦12.50bn, excluding major grid extension and battery |

Conclusion. The estimates are internally consistent with Gennex’s published product prices and a complete EPC scope, but they remain preliminary. The strongest next step is to issue the same technical specification to Gennex and at least two comparable EPC contractors, then compare their itemised bills of quantities on a like-for-like basis.

# References

• [1] Gennex Technologies homepage – company solutions and service scope — https://gennextechnologies.com/

• [2] Gennex Solar Projects – commercial project portfolio — https://gennextechnologies.com/solar-projects/

• [3] Petrocam solar installation project – disclosed site capacities — https://gennextechnologies.com/petrocam-solar-installation-project/

• [4] Jinko 725W bifacial module – published product price and specifications — https://gennextechnologies.com/725w-solar-panel-jinko-bifacial-module/

• [5] Gennex inverter category – 12kW inverter price reference — https://shop.gennextechnologies.com/product-category/gennex-inverters/

• [6] Gennex online store – 16kWh lithium battery price reference — https://shop.gennextechnologies.com/

• [7] IRENA, Renewable Power Generation Costs in 2024 — https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_2025.pdf

• [8] Electric Power Research Institute, The Impact of Solar PV DC:AC Ratio — https://restservice.epri.com/publicdownload/000000003002014245/0/Product

Source-access date: 16 July 2026. Online prices may change without notice. All arithmetic in this report uses the listed figures and rounds only where stated.